## Sheet1
Package | Subpackage | Activity | Subactivity | Unit_of_RFI | Optional_Qty_Unit | Inspection_Code | Inspection_Name | Inspection_Description | Checklist_Name | Is_Optional | Preceding_Inspection | Activity_Dependency
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.1 | Pre Pour Inspection - Grid Marking & Coordinate Checking | Grid Marking & Cordinate Checking | 1) C_9_1 Micro Pile Checklist of Fixed Tilt Structures | N | - | -
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.1 | Pre Pour Inspection - Grid Marking & Coordinate Checking | Grid Marking & Cordinate Checking | 2) C_14_1 Micro Pile Checklist of Tracker Structures | N | - | -
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.2 | Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring | Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wie and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | 1) C_9_2 Micro Pile Checklist of Fixed Tilt Structures | N | A.1.1.1
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.2 | Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring | Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wie and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | 2) C_14_2 Micro Pile Checklist of Tracker Structures | N | A.1.1.1
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.3 | Pile Capping - Pre-Pour | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | 1) C_9_2 Micro Pile Checklist of Fixed Tilt Structures | N | A.1.1.2
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.3 | Pile Capping - Pre-Pour | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | 2) C_14_2 Micro Pile Checklist of Tracker Structures | N | A.1.1.2
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.4 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A.1.1.3
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.5 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist | N | A.1.1.4
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.5 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | only testing report to be uploaded | N | A.1.1.4
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.1 | Pre Pour Inspection - Grid Marking & Coordinate Checking | Grid Marking & Cordinate Checking | C_9_1 Micro Pile Checklist of Fixed Tilt Structures | N | - | -
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.2 | Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring | Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wie and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 Micro Pile Checklist of Fixed Tilt Structures | N | A1.2.1
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.3 | Pile Capping - Pre-Pour | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 Micro Pile Checklist of Fixed Tilt Structures | N | A1.2.2
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.4 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A1.2.3
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.5 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist | N | A1.2.4
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.5 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | only testing report to be uploaded | N | A1.2.4
Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.1 | Pre Pour Inspection - Grid Marking & Coordinate Checking | Grid Marking & Cordinate Checking | C_9_1 Micro Pile Checklist of Fixed Tilt Structures | N | - | -
Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.2 | Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring | Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wie and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 Micro Pile Checklist of Fixed Tilt Structures | N | A1.3.1
Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.3 | Pile Capping - Pre-Pour | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 Micro Pile Checklist of Fixed Tilt Structures | N | A1.3.2
Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.4 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A1.3.3
Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.5 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist | N | A1.3.4
Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.5 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | only testing report to be uploaded | N | A1.3.4
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.1 | Pre Pour Inspection - Grid Marking & Coordinate Checking | Grid Marking & Cordinate Checking | C_9_1 Micro Pile Checklist of Fixed Tilt Structures | N | - | -
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.2 | Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring | Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wie and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 Micro Pile Checklist of Fixed Tilt Structures | N | A1.4.1
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.3 | Pile Capping - Pre-Pour | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 Micro Pile Checklist of Fixed Tilt Structures | N | A1.4.2
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.4 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A1.4.3
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.5 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist | N | A1.4.4
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.5 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | only testing report to be uploaded | N | A1.4.4
Civil | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.1 | Pre Pour Inspection for Micro Piling - Grid Marking & Coordinate Checking | Grid Marking & Cordinate Checking | C_9_1 Micro Pile Checklist of Fixed Tilt Structures | Y | - | -
Civil | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.2 | Pre Pour Inspection for Micro Piling - Checking of Boring Dimensions, Leveling and Concrete Pouring | Checking of Boring , Dia and Depth of Bore, Checking of pile cage, Top level of cage, cover, preparation of starter and concrete pouring works. Concreting Works (Mixing points), if mixing thorugh Ajax Floori (not required for RMC) | C_9_2 Micro Pile Checklist of Fixed Tilt Structures | Y | A2.1.1
Civil | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.3 | Pre Pour Inspection for Column & Slab - Cast-in-Situ | Fixing of reinforcements (as per BBS), positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Cordinates & Location of opening, cut-outs (Size as per drawing) upto concreting works (mixing & pouring). | C_1_Pour Card | N | A2.1.2
Civil | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.4 | Post Pour Inspection for Column & Slab - Cast-in-Situ | Physical Dimension of structure as per drawing & appearnce (free of defect, deformations, etc.,.) and curing etc. | C_8_Post Pour Check | N | A2.1.3
Civil | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.5 | Canopy Erection with Sheeting after grouting | Fixing of nut & bolts in erected structure prior to final allignment check and tightening | C_11_Dimensional Assembly | N | A2.1.4
Civil | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.5 | Canopy Erection with Sheeting after grouting | Fixing of nut & bolts in erected structure prior to final allignment check and tightening | Fitup Check Report and Inspection of Structural Alignme | N | A2.1.4
Civil | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.6 | Grouting | Readiness of grouting area (hacking, cleaning, soaking, shuttering,mixing,cube sampling works), grout pouring and acceptance of grout cube strength test results | C_34_Grouting Works | N | A2.1.5
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.1 | Sub Grade Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.2 | Gravel filling | Filling of suitable size gravels / sand as per drawing (Approved source material, physically Tested as per SFQP & accepted by Quality) | C_27_Gravel Filling Works | N | A2.2.1
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.3 | Sand Relative Density Test | To check the relative density of sand | C_15_FDD Test by Sand Replacement Method | Y | A2.2.2
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.4 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying & finishing upto required level | C_36_PCC Works | N | A2.2.3
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.5 | Pre Pour Inspection for Raft | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and upto concreting works | C_1_Pour Card | N | A2.2.4
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.6 | Post Pour Inspection for Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.2.5
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.7 | Pre Pour Inspection for Ist Lift Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Shuttering tightness, verticality, alignment checking prior to concreting and concreting works | C_1_Pour Card | N | A2.2.6
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.8 | Post Pour Inspection for Ist Lift Wall | Physical Dimension of structure & location of supported super-structures as per drawing,curing & appearnce (free of defect, deformations, etc.,.) and appllication of protecting coating paint | C_8_Post Pour Check | N | A2.2.7
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.9 | Backfiling Layer Wise | Layer-wise filling, compaction & testing in each layer untill achieving accepted test result. | C_16_FDD Test by Core Cutter Method | N | A2.2.8
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.10 | Pre Pour Inspection for 2nd Lift Wall with Rail | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Shuttering tightness, verticality, alignment checking prior to concreting and concreting works | C_1_Pour Card | N | A2.2.9
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.11 | Post Pour Inspection for 2nd Lift Wall with Rail | Physical Dimension of structure & location of supported super-structures as per drawing,curing & appearnce (free of defect, deformations, etc.,.) and appllication of protecting coating paint | C_8_Post Pour Check | N | A2.2.10
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.3.1 | Sub Grade Compaction Test & Leveling | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.3.2 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level | C_36_PCC Works | N | A2.3.1
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.3.3 | Pre Pour Inspection for RCC Block | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and concreting works | C_1_Pour Card | N | A2.3.2
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.3.4 | Post Pour Inspection for RCC Block | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.3.3
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.4.1 | Sub Grade Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.4.2 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level and concreting works | C_36_PCC Works | N | A2.4.1
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.4.3 | Pre Pour Inspection for Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment concreting works | C_1_Pour Card | N | A2.4.2
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.4.4 | Post Pour Inspection for Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.4.3
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.5.1 | Levelling & Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.5.2 | Rubble Soling Test | Laying of requisite size rubble soling material upto compaction | C_27_Gravel Filling Works | N | A2.5.1
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.5.3 | Pre-pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level and concreting works | C_36_PCC Works | N | A2.5.2
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.5.4 | Pre Pour Inspection for Raft | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment concreting works | C_1_Pour Card | Y | A2.5.3
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.5.5 | Post Pour Inspection for Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) with rectifications if any. And appllication of protecting coating paint | C_8_Post Pour Check | Y | A2.5.4
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.5.6 | Pre Pour Inspection for Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment, and upto concreting works | C_1_Pour Card | Y | A2.5.5
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.5.7 | Post Pour Inspection for Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectifications ofdefects if any. And appllication of protecting coating paint | C_8_Post Pour Check | Y | A2.5.6
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.5.8 | Pre Pour Inspection for Slab | Fixing & tighntness of shuttering supports, leak-proof arranegments, Reinforcement fixing, positioning of pockets/inserts/embedments. And upto concreting works | C_1_Pour Card | Y | A2.5.7
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.5.9 | Post Pour Inspection for Slab | Surface level/slope & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectification of defects if any | C_8_Post Pour Check | Y | A2.5.8
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.5.10 | Leak Test (If any), Rectification of defects (if any) & Acceptance of corrections action taken | Leak Test | C_8_Post Pour Check | Y | A2.5.9
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.6.1 | Sub Grade Compaction Test (including rubble soiling) | Levelling & compaction test of base & Laying of rubble | C_16_FDD Test by Core Cutter Method | N | - | -
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.6.2 | Pre Pour Inspection for Sump PCC | Level & Grid Marking for PCC Laying & finishing upto required level and concreting works | C_36_PCC Works | N | A2.6.1
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.6.3 | Pre Pour Inspection for Sump Raft | Fixing of reinforcements as per drawing prior to shutter board fixing, positioning of inserts & embedments (if any) and concreting works | C_1_Pour Card | N | A2.6.2
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.6.4 | Post Pour Inspection for Sump Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.6.3
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.6.5 | Pre Pour Inspection for Dyke Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment, and upto concreting works | C_1_Pour Card | N | A2.6.4
Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.6.6 | Post Pour Inspection for Dyke Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectifications ofdefects if any. And appllication of protecting coating paint | C_8_Post Pour Check | N | A2.6.5
Civil | MMS Installation | MMS Installation | MMS Installation | Per Table | MT | B1.1.1 | If Tracker: Tracker Alignment, Tightening & Torquing up to Torque Tube incl. Transmission Shaft If Fixed Tilt: Fixed Tilt Alignment, Tightening & Torquing up to bracing, perlin and all asembly parts | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts ) | 1) C_28_1 PV Module Mounting Structure Installation Protocol- Fixed Tilt | N | A.1.1.4
Civil | MMS Installation | MMS Installation | MMS Installation | Per Table | MT | B1.1.1 | If Tracker: Tracker Alignment, Tightening & Torquing up to Torque Tube incl. Transmission Shaft If Fixed Tilt: Fixed Tilt Alignment, Tightening & Torquing up to bracing, perlin and all asembly parts | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts ) | 2) C_29_1 PV Module Mounting Structure Installation Protocol - Tracker | N | A.1.1.4
Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Module Installation | Module Installation | Per Table | EA | C1.1.1 | If Tracker: Tracker: Module Alignment, Tightening & Torquing incl. U bolt & purlin If Fixed Tilt: Fixed Tilt: Module Alignment, Tightening & Torquing incl. purline | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts ) | 1) C_28_2PV Module Installation Protocol- Fixed Tilt | N | B1.1.1
Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Module Installation | Module Installation | Per Table | EA | C1.1.1 | If Tracker: Tracker: Module Alignment, Tightening & Torquing incl. U bolt & purlin If Fixed Tilt: Fixed Tilt: Module Alignment, Tightening & Torquing incl. purline | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts ) | 2) C_29_2 PV Module Installation Protocol - Tracker | N | B1.1.1
Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Robot Structure Installation | Installation of binders/clips, bridges, docking & reverse stations | Per Table | Not Applicable | C2.1.1 | Final Inspection of alignment, torquing of docking station, Flexible bridge, return station | Inspection Checklist for Installation of Cleaning Robot Structures | 1) Cleaning Robot Installation Checklist_Leapting | N | C1.1.1; A1.3.4
Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Robot Structure Installation | Installation of binders/clips, bridges, docking & reverse stations | Per Table | Not Applicable | C2.1.1 | Final Inspection of alignment, torquing of docking station, Flexible bridge, return station | Inspection Checklist for Installation of Cleaning Robot Structures | 2) Cleaning Robot Installation Checklist_Sol Bright | N | C1.1.1; A1.3.4
Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Robot Structure Installation | Installation of binders/clips, bridges, docking & reverse stations | Per Table | Not Applicable | C2.1.1 | Final Inspection of alignment, torquing of docking station, Flexible bridge, return station | Inspection Checklist for Installation of Cleaning Robot Structures | 3) Cleaning Robot Installation Checklist_Airtouch | N | C1.1.1; A1.3.4
Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Fencing | Block | Not Applicable | C3.1.1 | Fencing pole concrete | Markig of locations of posts, hole depth, Alignment, Verticality & level of Fence Post & concreting works as per drawing | C_47 USS | N | D1.1.3; D1.2.2; D1.3.2; D1.4.2; D1.5.1; D2.1.1
Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Fencing | Block | Not Applicable | C3.1.1 | Fencing pole concrete | Markig of locations of posts, hole depth, Alignment, Verticality & level of Fence Post & concreting works as per drawing | IDT.PSS Fencing Concrete Pole Works | N | D1.1.3; D1.2.2; D1.3.2; D1.4.2; D1.5.1; D2.1.1
Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Fencing | Block | Not Applicable | C3.1.2 | Fixing of Fencing wire, concertina, Gates as per drawing with painting | Fixing of Fencing wire, concertina, Gates as per drawing with painting | C_10_Installation & Erection of Honey Comb Fence Post & Accessories | N | C3.1.1
Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Gravel Laying | Block | Not Applicable | C3.2.1 | Gravel filling | Inspection of Gravel Filling Works | C_27_Gravel Filling Works | N | C3.1.2
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.1 | IDT and Accessories Installation | IDT Installation along with Accessories | A1_IDT and Accessories Installation | N | A2.2.11
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.2 | IDT Electrical & Oil Filtration Testing | Electrical and Oil Filtration testing of IDT after installation | A2_IDT Oil Filled Transformer Oil Filtration and Testing | N | D1.1.1
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.2 | IDT Electrical & Oil Filtration Testing | Electrical and Oil Filtration testing of IDT after installation | + | N | D1.1.1
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.2 | IDT Electrical & Oil Filtration Testing | Electrical and Oil Filtration testing of IDT after installation | Upload of 3 testing reports | N | D1.1.1
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.3 | Inverter Cable Terminations & Equipment Earthing | LT and Control Cable Lugging, Crimping, Sleeving, HV side HT cable end termination, Torquing, Equipment body Earthing | A3_IDT Oil Filled Transformer HT | N | D1.1.2
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.3 | Inverter Cable Terminations & Equipment Earthing | LT and Control Cable Lugging, Crimping, Sleeving, HV side HT cable end termination, Torquing, Equipment body Earthing | LT and Control Cable Termination | N | D1.1.2
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.3 | Inverter Cable Terminations & Equipment Earthing | LT and Control Cable Lugging, Crimping, Sleeving, HV side HT cable end termination, Torquing, Equipment body Earthing | Equipment Earthing | N | D1.1.2
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | HT Panel | Block | EA | D1.2.1 | HT Panel Installation & Testing | Panel installation and Panel testing | C1_HT Panel Installation & Testing | N | A2.1.6
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | HT Panel | Block | EA | D1.2.1 | HT Panel Installation & Testing | Panel installation and Panel testing | + | N | A2.1.6
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | HT Panel | Block | EA | D1.2.1 | HT Panel Installation & Testing | Panel installation and Panel testing | Upload of Testing Report | N | A2.1.6
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | HT Panel | Block | EA | D1.2.2 | HT Panel Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, HT cable end termination, Torquing, Equipment body Earthing | C2_Cable Termination & Equipment Body Earthing | N | D1.2.1
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | LT Panel | Block | NO | D1.3.1 | LT Panel Installation & Testing | Panel installation and Panel testing | B1_LT Panel Installation & Testing | N | A2.1.6
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | LT Panel | Block | NO | D1.3.1 | LT Panel Installation & Testing | Panel installation and Panel testing | + | N | A2.1.6
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | LT Panel | Block | NO | D1.3.1 | LT Panel Installation & Testing | Panel installation and Panel testing | Upload of Testing Report | N | A2.1.6
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | LT Panel | Block | NO | D1.3.2 | LT Panel Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, Torquing, Equipment body Earthing | B2_Cable Termination & Equipment Body Earthing | N | D1.3.1
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Auxiliary Transformer | Block | SET | D1.4.1 | Auxiliary Transformer Installation & Testing | Auxiliary transformer installation as per OEM Manual/Drawing and Testing | D1_Auxiliary Transformer Installation & Testing | N | A2.3.4
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Auxiliary Transformer | Block | SET | D1.4.1 | Auxiliary Transformer Installation & Testing | Auxiliary transformer installation as per OEM Manual/Drawing and Testing | + | N | A2.3.4
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Auxiliary Transformer | Block | SET | D1.4.1 | Auxiliary Transformer Installation & Testing | Auxiliary transformer installation as per OEM Manual/Drawing and Testing | Upload of Testing Report | N | A2.3.4
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Auxiliary Transformer | Block | SET | D1.4.2 | Auxiliary Transformer Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, Torquing, Equipment body Earthing | D2_Cable Termination & Equipment Body Earthing | N | D1.4.1
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | NIFPS | Block | LOT | D1.5.1 | NIFPS Installation & Testing | NIFPS Installation & Testing | No Checklist | Y | A2.4.4
Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | NIFPS | Block | LOT | D1.5.1 | NIFPS Installation & Testing | NIFPS Installation & Testing | only testing report to be uploaded | Y | A2.4.4
Electrical | AC / LT Network | AC/LT Network - Cable & Cable Management System Laying | LT Cable Laying - Inverter to LT Panel | Per Inverter | M | D2.1.1 | Cable drum IR test and Cable hanging for above-ground section | Cable drum IR test and Cable hanging for above-ground section | F1_1 Cable Drum IR test | N | A1.4.4
Electrical | AC / LT Network | AC/LT Network - Cable & Cable Management System Laying | LT Cable Laying - Inverter to LT Panel | Per Inverter | M | D2.1.1 | Cable drum IR test and Cable hanging for above-ground section | Cable drum IR test and Cable hanging for above-ground section | Cable Hanging | N | A1.4.4
Electrical | AC / LT Network | AC/LT Network - Cable & Cable Management System Laying | LT Cable Mgmt System Laying | Block | Not Applicable | D2.2.1 | Messenger wire hanging | Messenger wire hanging | F1_2 Messenger Wire Hanging | N | A1.4.4
Electrical | AC / LT Network | AC/LT Network - Earthing | Grid Earthing | Block | M | D3.1.1 | Grid Earthing work & Testing | Grid Earthing work & Testing | H4_Grid Earthing | N | D1.1.3; D1.2.2; D1.3.2; D1.4.2; D1.5.1
Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter | Per Inverter | NO | E1.1.1 | Inverter Installation, Testing & Equipment Earthing | Inverter installation; Equipment body Earthing | H3_String Inverter Installation & Earthing | N | A1.2.4
Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter - LT Cable Termination | Per Inverter | NO | E1.2.1 | LT Cable termination at inverter | LT Cable Lugging, Crimping, Sleeving & Torquing | F3_ LT Cable Termination | N | D2.1.1; E1.1.1
Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter - String Formation | Per Inverter | NO | E1.3.1 | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | H2_MC4 Connection | N | C1.1.1
Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter - String Formation | Per Inverter | NO | E1.3.1 | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | VOC Testing | N | C1.1.1
Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter - String Formation | Per Inverter | NO | E1.3.1 | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | Cable Dressing | N | C1.1.1
Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter - String Formation | Per Inverter | NO | E1.3.1 | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | Ferrule Checking and PU Foam Sealing | N | C1.1.1
Electrical | DC Network | DC Network - Cable Laying | DC Cable Works | Per Inverter | M | E2.1.1 | Trench excavation, DC cable laying, dressing, conduiting and PU foam sealing | Trench excavation, DC cable laying, dressing, conduiting (Modules to Inverter) | H1_Trench Excavation | N | C1.1.1
Electrical | DC Network | DC Network - Cable Laying | DC Cable Works | Per Inverter | M | E2.1.1 | Trench excavation, DC cable laying, dressing, conduiting and PU foam sealing | Trench excavation, DC cable laying, dressing, conduiting (Modules to Inverter) | DC Cable Laying and Conduiting | N | C1.1.1
Electrical | DC Network | DC Network - Earthing | Earthing of tables | Per Table | M | E3.1.1 | Table-to-table & grid earthing work testing | Table-to-table & grid earthing work testing | H4_Grid Earthing | N | B1.1.1